ALUMINUM WEATHERPROOF ENCLOSURE

SAMPLE SPECIFICATIONS

INTENT:

The intent of this specification is to provide the owner with a generator set enclosure complete in every detail and requiring no additional in-field modifications or assembly, except where specifically allowed by these specifications. The enclosure is to be accurately dimensioned so as to be in compliance with the National Electrical Code (NEC), and the National Fire Protection Association (NFPA) for clearance of all specified items included therein, and all applicable fire codes for a structure and application of this type.

Construction drawings, engineering blueprints, or other bid documents accompanying these specifications which show switchgear, transfer switch(es), motor controller(s) and/or other service or distribution equipment within the generator set enclosure must be considered complimentary to and not in lieu of this written specification. Drawings submitted for approval shall reflect this fact clearly and any contradiction or omission shall be brought to the attention of the designing engineer prior to order.

CONSTRUCTION:

The weatherproof enclosure shall be of formed aluminum panel construction as designed and manufactured by Robinson Custom Enclosures. The enclosure is rated to a wind load of 120 MPH (150 MPH optional) and 50lbs./sq ft roof load. Rain test equal to 4 inches/hour. The basic structure meets all seismic requirements of Zone 4 or equivalent. The design and construction shall be modular in that the panels shall not exceed 24” in width and shall be minimum thickness of 0.125 gauge. Doors shall not exceed 36” in width and be a minimum of 0.125 gauge. The roof of the enclosure shall meet or exceed the minimum gauge requirements specified but, in addition, shall be strengthened in such a manner as to support the largest commercially available exhaust silencer recommended by the engine manufacturer for this application. All exterior components of the enclosure shall be assembled utilizing stainless steel bolts, nuts and lock washers. All seams shall be sealed to prevent leaks.

DOORS:

All doors on the enclosure shall be strategically located in areas as to allow ease of maintenance on the generator set and allow good access to and visibility of instruments, controls, engine gauges, etc. The doors shall be fitted with stainless steel bolt-on, lift off hinges with pins of a diameter not less than .375”. Each door shall be fitted with flush-mounted, key lockable latches or pad lockable latches. The latch hardware shall allow escape from within when locked externally. Door holdback hardware shall be provided to secure the door to the enclosure wall during installation and maintenance. All doors shall be gasketed to prevent leaks.

COOLING:

Under no circumstances shall the floor area or any of its parts be considered for cooling air intake or discharge requirements of the generator set or its associated equipment.

WALKAROUND PROVISIONS:

An aisle, at least 24” wide, shall be provided on each side of the generator set and an extra 36” behind the generator set shall be included. Space occupied by the day tank shall not interfere with the aisle requirements.

SOUND ATTENUATION:	(Optional)

The entire enclosure except for the louvered openings shall have acoustic material installed on the interior roof and wall panels of a weight and thickness consistent with the specified level of noise reduction. The acoustic material shall be held in place by galvanized perforated metal sheeting to form a removable section easily inspected by maintenance personnel.  The enclosure package shall be designed to achieve a 25 dBa sound rating when measured at a distance of 7 meters.

PAINT:

The enclosure shall be powder coated or prime painted with a minimum of two (2) coats of rust-inhibiting primer and finished with a minimum of two (2) coats of polyurethane.

LOUVERS:

All louvers shall be designed to help prevent the entrance of driving rainwater, but shall have sufficient free area to allow for engine-generator cooling air requirements.

LOAD CENTER:             	(Optional)

The enclosure shall be equipped with a 100amp 240/120-volt single-phase load center for the battery charger, jacket water heater(s), lighting, receptacles, etc., as specified and as shown on the drawings. The load center shall be mounted within the enclosure and allow for a single entry point for commercial power supply conduit and wiring by the installing contractor. The placement of this load center shall be shown on the submittal drawings. All internal conduit and wiring to the various ancillary equipment supplied with the package and shall be pre-wired by Robinson Custom Enclosures in accordance with all governing codes pursuant to this application. The load center shall be considered as part of the emergency load and shall derive its power source downstream from the load transfer switch specified elsewhere. If a step-down transformer is required, to be placed ahead of this load center, it together with a properly sized protective device shall be supplied and installed by Robinson Custom Enclosures within the enclosure.

INTERNAL WIRING:

All wiring within the enclosure shall be in conduits made from rigid metal, EMT, or liquid-tight material specifically manufactured for electrical use. All connections at the generator set shall be flexible, and all shall be provided and installed by Robinson Custom Enclosures.

MOTORIZED LOUVERS:                   (Optional)

Air intake and exhaust louvers shall be of aluminum construction. The louvers shall open automatically upon diesel generator start and close upon diesel generator shutdown. Heavy-duty screens over the intake louvers shall be provided.

INTERIOR INCONDESCENT LIGHTING: (AC)          (Optional)

Vapor proof lights shall be installed within the enclosure and strategically located on either side of the generator set. They shall be ceiling mounted and parallel to the length of the unit. Their AC power source shall be taken from the commercial power supply at the job-site and wired-in by way of the load center specified elsewhere. The light switch box, located by one of the entrance way doors, shall have its own grounded duplex receptacle mounted therein for use by maintenance personnel.

INTERIOR LIGHTING: (DC)                  (Optional)

A battery operated vapor proof light deriving its power from the engine cranking batteries shall be installed in a strategic location within the enclosure and shall be controlled by a switch located by one of the entrance doors. The light shall be large enough to provide illumination in an emergency situation yet not such an overburdening drain will be placed on the starting batteries. The switch controlling this light shall be a wind-up timer type, which automatically shuts off after a preset interval not to exceed one hour.

INTERIOR FLUORESCENT LIGHTING: (AC)          (Optional)

Forty-eight”, dual-tube fluorescent lights shall be installed within the enclosure and strategically located on either side of the generator set. They shall be ceiling mounted and parallel to the length of the unit. Their AC power source shall be taken from the commercial power supply at the job-site and wired-in by way of the load center specified elsewhere. The light switch box, located by one of the entranceway doors, shall have its own-grounded duplex receptacle mounted therein for use by maintenance personnel.

EXTERIOR LIGHTING:                     (Optional)

The enclosure shall be equipped with a light on the exterior of the building, wired into the commercial power supply load center, and activated automatically by way of a photoelectric cell which will switch the light on during evening hours and off during daylight hours. The fixture for the light shall be of vandal-proof design, mounted above one of the side doors.

EXHAUST FAN:                                   (Optional)

The enclosure is to be fitted with a 120-volt shutter mounted exhaust fan with control

SPACE HEATER:	(Optional)

The enclosure is to be fitted with 5kW, 240V, single phase space heater complete with a thermostat.

RUNNING BEACON:           	 (Optional)

A weatherproof, rotating beacon light shall be mounted atop the enclosure and wired to operate off generator output voltage or battery voltage each time the generator runs. This beacon shall be amber in color.

FAULT BEACON: 	 (Optional)

A weatherproof, rotating beacon light and police type siren shall be mounted atop the enclosure and wired to operate off battery voltage in the event of an engine fault or alarm condition. This beacon will be red in color, and the siren shall be wired to the alarm silence switch in the generator control panel.

THERMO INSULATION:	(Optional)

The enclosure is to be thermo insulated with gasketed doors. Insulation material is to be fiberglass held in place with a galvanized perforated metal liner.

OIL & RADIATOR DRAINS:              (Optional)

All necessary fittings, hoses, shut-off valves, etc., shall be provided by Robinson Custom Enclosures to facilitate lube oil and radiator drain at the exterior of the enclosure. In addition, engines equipped with crankcase breather tubes shall have this tube terminate at the exterior of the enclosure.

ENCLOSURE FLOORING:                 (Optional)

The floor of the enclosure shall be designed and constructed in such a manner as to prevent the entrance of rodents. This shall be accomplished with solid metal or “diamond plate” but, in any event, must be capable of fully supporting any ancillary equipment specified which may be secured to it plus the anticipated weight of maintenance personnel and their tools.

SKID BASE MOUNTING:

The generator set and enclosure shall be mounted and shipped to the engine dealer on the structural steel skid base manufactured by Robinson Custom Enclosures. Provisions for crane unloading of the complete package shall be designed into the base of the unit.

CLEARANCE – The base and enclosure assembly shall allow room within the package to mount and maintain the specified battery charger, engine starting batteries, racks and cables, main line circuit breaker, engine-generator control panel, and other items as specified or as shown on the drawings.

WEIGHT – The weight of the entire unit consisting of generator set, base, enclosure and other specified items including all liquids (i.e., fuel oil and cooling solutions) shall be calculated by the engine dealer utilizing manufacturer’s data. The base of the unit shall be designed and manufactured as a heavy duty, structural steel construction with lifting provisions to support the calculated weight. Details of the base construction shall be included with the drawings submitted for approval as well as all dealer weight calculations supported by manufacturer’s data.

BASE TANK:

The unit shall be equipped with a UL-142 labeled sub base fuel tank of 4300 gallon minimum capacity and shall be supplied with a lockable fill cap. All necessary vent and fuel lines for proper engine performance shall be provided as well as a means to readily detect the fuel level in the tank without the use of a measuring stick.

CONTAINMENT BASIN:

The unit shall be equipped with a fuel containment basin with a normal capacity of 110% of the main fuel tank and shall be supplied with a leakage detector switch in the basin and wired to an indicating light on the generator control panel.

LOW FUEL INDICATOR:

The fuel tank shall be fitted with a low fuel level alarm, which shall be wired to an indicating light on the generator control panel of the generator set. This switch shall activate whenever the fuel level in the tank is 20% or less remaining.

EXHAUST SILENCER – Internal silencer shall be mounted by Robinson Custom Enclosures according to manufacturer’s recommendations. External silencer shall be mounted at the job-site by the installing contractor when the silencer is loose-shipped due to height restrictions in transit. The silencer shall be mounted such that its weight is not supported by the engine nor will exhaust system growth due to thermal expansion be imposed on the engine. Exhaust pipe sizes shall be sufficient to ensure that exhaust backpressure does not exceed the maximum limitations specified by the engine manufacturer.

TAIL PIPE:

Each silencer shall be fitted with a 90° tail pipe extension (elbow) terminating in a vertical position and, to prevent the entrance of rainwater, shall be fitted with a weighted, rain cap.

RAIN SKIRT:

At the point where the exhaust pipe penetrates the roof of the enclosure, a suitable “rain skirt” and collar shall be provided by Robinson Custom Enclosures. It shall be designed to prevent the entrance of rain yet allow for expansion and vibration of the exhaust piping without chafing or stress to the exhaust system.

BATTERY TRAY:

A battery tray shall be provided for the batteries and shall conform to NEC 480-7 (b). It shall be constructed and so treated as to be resistant to deterioration by battery electrolyte. Further, construction shall be such that any spillage or boil-over of battery electrolyte shall be contained within the tray to prevent a direct path to ground. A separate tray shall be provided for each battery bank and placed on each side of the engine on all dual starter motor equipped units.

BATTERY CHARGER:                          (Optional)

A current limiting, automatic DC battery charger shall be furnished to automatically recharge the batteries.

FIRE DETECTION AND SURPRESSION SYSTEMS: (Optional)

The fire suppression shall be a CO2 system.

GAS DETECTION SYSTEMS: (Optional)

WIRING AND CONNECTORS:

All conduits, wire, cables, interconnections, etc., entering or exiting the generator enclosure shall be furnished and installed by the installing contractor. All wiring shall be in conduits sized in accordance with the NEC. All power wiring shall be THW copper. All control wiring shall be standard type THHN-THWN copper. All power and control wiring shall be installed for a complete and operating system.

LOAD BANK TESTING:

The load bank will be capable of definite and precise incremental loading and shall not be dependent on the generator control instrumentation to read amperage, voltage, or frequency. Rather, the test instrumentation will serve as a check of the generator set meters. Further, the load bank shall be power factor matched to the rating of the generator set as shown in the manufacturer’s published data and as specified for this project.

WARRANTY:

Equipment furnished under this Section shall be guaranteed against defective parts and workmanship under the terms and conditions of the manufacturer and dealers standard warranty. But, in no event shall it be for a period of less than one year from date of initial start-up of the system and shall include labor and travel time for necessary repairs at the job-site. Submittal start-up data received without written warranties as specified will be rejected in their entirety.